## Slide 1: RTDS-Based Supervisory Control Performance Verification for AC Multiple-Microgrid Systems
  Presenter: Arman Ghasaei
  October 2020

## Slide 2: Preface:
  The work in this presentation is part of my Ph.D. dissertation under the supervision of Professor Reza Iravani.
  The RTDS simulation platform used in the work is a property of Center of Applied Power Electronics (CAPE) at University of Toronto.

## Slide 3
i
Why microgrid? Motivations and challenges?
ii
Multiple-microgrid system? Value proposition?
iii
The hierarchical supervisory control system
iv
Supervisory control performance verification via RTDS-PLCnext platform
Why supervisory control?
Application for first nation communities in North-West Ontario
Outline:
1

## Slide 4
Motivations
Supervisory control system
Performance verification
Multiple-microgrid system
Industrial loads
Residential loads
Transmission
line
EV charging
stations
Renewable energies
Microgrid
Legacy distribution power system is changing:
* Renewables (intermittent generations)
* EV stations (intermittent loads)
No coordination anti-islanding policies!
Microgrid:
Autonomy of operation from the utility
Key component: storage system (fast, bi-directional, dispatchable)
2
Storage system
E? P?
Distribution system

## Slide 5
Industrial loads
Residential loads
Transmission
line
Storage system
EV charging
stations
Intelligence
(Supervisory Control)
Renewable energies
measurements
commands (CMD)
Microgrid
SCADA
Intelligence (supervisory control):
Energy trading
Emergency power provision (more reliability)
Islanded operation (more resiliency)
It is all about a functional supervisory control system!
$
P
3
$
E
V-f
P-Q
SOC
Motivations
Supervisory control system
Performance verification
Multiple-microgrid system
local control
local control
local control
local control
CMD
CMD
CMD
CMD
CMD
CMD

## Slide 6
: SOC? operational?
: sunny? cloudy?
: Windy?
: EV #?
(2 operation condition)/(component):
131072 possible scenarios for supervisory control to cover!
4
Motivations
Supervisory control system
Performance verification
Multiple-microgrid system

## Slide 7
5
Envisioned Modes of Operation |  | 
CBm | Closed | Grid-connected
 | Open | Islanded
CBi,(i=1,2,3,4) | Closed | Grid-connected MG or islanded multiple-microgrid system
 | Open | Islanded single-microgrid
Islanded
Three-Microgrid System
Islanded Single-Microgrid System
Three independently
controlled grid-connected MGs
Motivations
Supervisory control system
Performance verification
Multiple-microgrid system

## Slide 8
Northwest Ontario Bulk Planning Initiative (IESO-Hydro One-Next Bridge)
Remote generation 9-10 times higher cost vs provincial generation
($1.14/kWh VS $0.12/kWh)
Source: (OPA)
475 MW capacity increase
Source: (IESO)
Anticipated cost reduction:
1.5 B $/year!
New 230 kV lines
Source: IESO
Existing East-West Tie
Existing West of Thunder Bay Transmission System
6
Motivations
Supervisory control system
Performance verification
Multiple-microgrid system

## Slide 9
First nation community sub-systems:
7
Source: Agoracom.com
Motivations
Supervisory control system
Performance verification
Multiple-microgrid system

## Slide 10
Value proposition:
1) Benefit from clean energy
2) Energy trading with utility
2) Emergency energy support
3) Enhanced security of supply
8
$
E
$
E
$
E
$
E
$
P
$
P
$
P
$
P
Islanded Single-Microgrid System
Islanded Four-Microgrid
System
Islanded Three-Microgrid
System
Motivations
Supervisory control system
Performance verification
Multiple-microgrid system

## Slide 11
Does the SC system provide a trivial task?
Multi-microgrid components | 
#4 | 13 MW 13 MWh
#12 | 20 MW Replacing each 5 MW diesel-fuel saves 20 M$/year
#2 | 12 MW ONLY BAKCUP
 | Average: 17 MW Peak: 31.9 MW
9
Motivations
Supervisory control system
Performance verification
Multiple-microgrid system

## Slide 12
10
All should be covered by the SC system!
For this system of 5 CBs
32 possible CB configurations
Complexity of operation?
Motivations
Supervisory control system
Performance verification
Multiple-microgrid system

## Slide 13
Within each MG:
coordination
SC System
11
Motivations
Supervisory control system
Performance verification
Multiple-microgrid system

## Slide 14
SC: Supervisory Control
CB: Circuit-Breaker
MG: microgrid
CMD: command
MMT: measurement
Two-layer Hirarchical SC system:
12
Motivations
Supervisory control system
Performance verification
Multiple-microgrid system

## Slide 15
Existing methods for SC
13
Heuristic-based development! All scenarios?
Solution for each scenario?
Non-blocking?
Scalable?
Large-scaled systems?
Multiple flow-charts and confliction!?
Not automated!
Source: https://www.reddit.com/r/witcher/comments/396om2/can_someone_make_a_flow_chart_of_the_characters/
?
?
?
?
?
?
?
?
?
?
?
?
Motivations
Supervisory control system
Performance verification
Multiple-microgrid system

## Slide 16
Supervisory Control Theory (SCT)
Systematic development
Guaranteed to covers all possible scenarios
In case of an event: provides an operation solution
Non-blocking
Non-conflicting
Scalable
Automated solution!
14
Motivations
Supervisory control system
Performance verification
Multiple-microgrid system

## Slide 17
SCT-based SC System
Multiple-Microgrid Model
Proposed Control
Strategy
SCT-based design tool
15
Storage system
SOC
P-Q
V-f
non-blocking
non-blocking
non-blocking
non-conflicting
non-conflicting
non-conflicting
48 decentralized
supervisors
Motivations
Supervisory control system
Performance verification
Multiple-microgrid system

## Slide 18
Verification of PLCnext performance?
Supervisory control design
Off-line evaluation
Real-time verification
Field test
PSCAD
/
EMTDC
Multiple microgrid
and local control
MATLAB
–
Stateflow
Supervisory control
RTDS
Multiple microgrid
and local control
PLCNext
HIL
MMT
CMD
MMT
CMD
16
SC
algorithm
Motivations
Supervisory control system
Performance verification
Multiple-microgrid system

## Slide 19
HIL
17
Real-time simulation of roughly 600 electrical nodes and 18 distributed resource
Δt = 80 us
Motivations
Supervisory control system
Performance verification
Multiple-microgrid system

## Slide 20
RTDS (80 us)
Analog Cards
Digital Cards
Fiber Connection
(1 ms) PLCNext
Digital Modules
Analog Modules
Digital to RTDS # 31
PB5 # 19
Digital to PLCnext # 5
Analog to PLCnext # 26
Analog to RTDS # 4
MODBUS-TCP
Source: https://www.phoenixcontact.com/online/portal/ca?1dmy&urile=wcm:path:/caen/web/home
HIL
18
https://www.rtd.com/manuals.htm
Motivations
Supervisory control system
Performance verification
Multiple-microgrid system
GTNET Card

## Slide 21
Voltage support function
19
P,Q request
P1,Vref1
P2,Vref2
P3,Vref3
P4,Vref4
cmd
cmd
cmd
cmd
P
SCR = 12.2
SCR = 0.1
VPCCm
Q
T = 32.000 s
T = 32.030 s
T = 32.031 s
T = 32.041 s
T = 32.040 s
T = 32.050 s
Complying with IEEE-1547 standard

## Slide 22
Intentional islanding
cmd
cmd
cmd
cmd
T = 5.011 s
T = 5.012 s
T = 5.020 s
T = 5.021 s
T = 5.022 s
T = 5.023 s
T = 5.024s
T = 5.025 s
T = 5.026 s
T = 5.027 s
T = 5.028 s
20
T = 5.011 s
T = 5.012 s
T = 5.020 s
T = 5.021 s
T = 5.022 s
T = 5.023 s
T = 5.024 s
T = 5.025 s
T = 5.026 s
T = 5.027 s
T = 5.028 s
CBm-opening
Open CBm
Grid-forming cmd
Grid-forming cmd
Grid-forming cmd
Grid-forming cmd
SOC1
SOC2
SOC3
SOC4
State1
State2
State3
State4
Complying with IEEE-1547 standard
SCm
SC1
SC2
SC3
SC4
PCC1
PCC2
PCC3
PCC4

## Slide 23
Q&A
E-mail: arman.ghasaei@mail.utoronto.ca