## Slide 1: HVDC Factory Acceptance Tests supported by test automation using RSCAD Python API
Niklas Strunz
Siemens Energy

## Slide 2: Agenda
01
Introduction
Background and the HVDC RTS team
02
HiL verification and automation
Test environment, workflow and implementation
03
Execution challenges
Reconfiguration and automated evaluation
04
Automation in Factory Acceptance Tests
Scope, consistency, speed and customer benefits

## Slide 3: Introduction
Background
M.Sc. Energy Science and Technology
FAU Erlangen, 2022
Joined Siemens Energy in 2022
HVDC Control and Protection
HVDC RTS team
Our team’s focus
Dynamic grid and HVDC simulation
for HiL environments
HiL expertise
Replica planning and execution

## Slide 4: Basic HVDC system
HVDC = High-voltage direct current
1 Convert
Change AC power
into DC power.
2 Transmit
Carry power over
the DC connection.
3 Convert back
Supply AC power
to the receiving grid.
~
~
~
=
=
~
AC grid
AC grid
Sending end
Receiving end
Converter
Converter
AC to DC
DC to AC
DC transmission
=
Cable or overhead line
Notes: Basic explanation: AC means alternating current. DC means direct current. A converter station changes AC into DC. A cable or overhead line carries the power to another converter station, which changes it back into AC for the receiving grid. This simplified diagram shows one direction of power transfer and omits transformers, filters, switchgear, and control and protection equipment.
[Sources]
https://en.wikipedia.org/wiki/HVDC_converter_station
https://www.siemens-energy.com/global/en/home/stories/offshore-grid-access.html
https://www.siemens-energy.com/global/en/home/products-services/product-offerings/high-voltage-direct-current-transmission-solutions.html
[/Sources]

## Slide 5: HiL verification of HVDC control & protection
Verification scope
Actual control and protection
hardware and software
The real-time simulator supplies secondary measurement signals
Original hardware and I/O
Real-time simulator
C&P hardware
PC, BPC, DCP, Meas
Communication backbone
HMI
Measurements
Response
State information
Commands
State information
Commands

## Slide 6: Test automation in HiL environments
Conventional software tests
HiL automation
Requirements and test instructions
become executable test code
Test logic also maps actions and checks
to different communication interfaces
A controlled setup typically provides
a known starting state
The initial system state may be unknown
and needs explicit verification
HiL test automation sequence
1
Observe
Read the current state
2
Reconfigure
Establish the desired state
3
Verify
Confirm test preconditions
4
Execute
Run only when ready
5
Evaluate
Automated analysis of results
Notes: Based on the content supplied by the presenter. The comparison uses conventional software tests with a controlled setup as the baseline. Software automation can also involve multiple interfaces and uncertain state. HiL adds the need to coordinate interfaces and explicitly establish hardware/system preconditions. The preparation sequence is a proposed way to explain the reconfiguration question, not a verified implementation.

## Slide 7: Automation in our HVDC environment
Real-time simulator
C&P hardware
PC, BPC, DCP, Meas
Communication backbone
HMI
Measurements
Response
State information
Commands
State information
Commands
Simulator and operator-level control
Python automation
RSCAD Python API
HMI protocol
Direct backbone access using the same protocol and operator commands as the HMI
No C&P hardware and only minor software changes Less interference with the system

## Slide 8: Challenges in automated test execution
Reconfiguration and evaluation need the most attention
1
Observe
Established
Read required data through the established link.
2
Reconfigure
Key challenge
Project-specific topologies and transition paths.
3
Verify
Established
Check test preconditions using backbone data.
4
Execute
Established
Trigger events using simulator and system control.
5
Evaluate
Key challenge
Changing dynamics limit automatic result analysis.
Current assessment for this automation environment

## Slide 9: Reconfiguration between consecutive tests
Project topology determines which transitions are possible
Option 1: Reset and replay
Option 2: State machine
Reset to a defined state
(e.g. de-energized).
Follow a default path to the next test state.
Model valid reconfigurations.
Use system responses to identify allowed transitions and plan a sequence.
Main limitation
Abrupt, non-realistic changes can conflict with the real hard- and software.
Proposed approach
Reach the desired state through valid transitions rather than forced resets.

## Slide 10: Automated evaluation: capabilities and limits
Complex dynamic tests
Dynamics vary from test to test. Our current implementation cannot yet evaluate complex dynamic tests automatically.
Selected regression tests support automatic checks
A fixed acceptance rule, such as a constant ramp rate or a prohibited event, makes the result check explicit.
Power ramp
Check a constant ramp rate
of 50 MW/min
Protection tests
Compare test to expected high level behavior

## Slide 11: Automation scope in FAT
Software integrity remains the priority
Retain HMI-based functional tests
Automate repetitive test cases
Basic operating sequences
Integrity of operator inputs
Fault ride-through scenarios
Protection tests
These tests must include the HMI.
Direct backbone access bypasses it and cannot verify its behavior.
Here, the HMI only helps establish the test state. Automation can perform that setup and execute the test.

## Slide 12: Repetitive FAT: consistency and speed
More consistent execution
Repeat programmed sequences consistently, reducing manual entry errors and variation between runs.
Faster configuration
Programs can set hundreds of values per second.
Manual HMI input is slower and ties up test personnel.
Same test outputs
and report format
Automation retains the outputs and test report used for manual execution. Complex results still require expert analysis.

## Slide 13: Q&A